## Introduction
| 1396/10/22 | Date:
| 38.3 | Revision
Ali Cheraghi
یا حق
مقدمه
1. این نرم افزار کوچک آموزشی اولین بار در سال 1386 در شرکت نور ندا سیستم و بجهت آموزش پرسنل تهیه گردید و سپس در سال های بعد اصلاحاتی در آن بوجود آمد. 2. این افزار کوچک قادر به محاسبه اولیۀ حجم گاز و تعداد کپسول های محتوی گاز FM-200، مورد نیاز در سیستم های اطفاء حریق اتوماتیک پایۀ گاز می باشد. 3. هدف از ایجاد این نرم افزار، آموزش محاسبه حجم گاز، سرعت بخشیدن به محاسبۀ اولیۀ حجم گاز و تعداد کپسول های مورد نیاز می باشد. 4. محاسبات نهایی و اصلی می بایست توسط نرم افزارهای مربوطه همانند نرم افزارهای شرکت TYCO-THORN-LPG انجام شود. 5. استفاده از این نرم افزار نیازمند آشنایی کامل با استاندادرهای مربوطه همانند NFPA2001، خصوصیات و رفتار گاز مورد نظر و سایر کدها و الزمات مربوطه می باشد. 6. انجام محاسبات باید توسط افراد آشنا با مهندسی حریق و آموزش دیده انجام شود. 7. در صفحه خلاصه (summary)، سلول های خالی با فونت بنفش رنگ و در سایر صفحات، سلول های با فونت سبز و بنفش رنگ جهت ورود اطلاعات (اعم از تایپ و یا انتخاب گزینه) در نظر گرفته شده اند. 8. در تمامی صفحات سلول های با فونت آبی رنگ نتایج محاسبات بوده و غیر قابل تغییر می باشند. 9. برای هر بار محاسبه، صفحات باید بترتیب مرور و اطلاعات لازم در هر سطر بترتیب از بالا به پایین کامل شود. 10. به هشدارهای داده شده و یا اطلاعات تکمیلی (comment) ارائه شده، توجه کامل شود.
از جناب استاد مهندس مرتضی خلیل پیما، مدیریت محترم عامل شرکت نور ندا بعلت آموزش ها و راهنمایی های همیشگی شان در مسیر آشنایی با مهندسی حریق، کمال تشکر و قدردانی را دارم. از جناب آقای مهندس امیر خلیل پیما، مدیریت محترم عامل شرکت نور ندا سیستم بعلت مساعدت و پشتیبانی همه جانبه در جهت آموزش و همچنین ایجاد این نرم افزار و سایر مقالات مرتبط با مباحث مهندسی حریق سپاسگذارم. این نرم افزار کوچک وقف عام بوده و استفاده از آن با ذکر منبع برای تمامی افراد و سازمان ها بلامانع می باشد. از تمامی دوستان، اساتید و کارشناسان محترم تقاضا دارم تا پس از استفاده از این نرم افزار، با ارائه انتقادات، پیشنهادات و راهنمائی های خود اینجانب را در برطرف نمودن ایرادات موجود و ارتقاء این نرم افزار یاری فرمایند.
شاد زی ، مهر افزون
علی چراغی
(تهران هفتم خرداد ماه 1396)
راه های تماس:
|  | ali@noorneda.com ali_cheraghi@yahoo.com | Email:
|  | +98 912 376 1057 | Cellphone:
آشنایی با سیستم اطفاء حریق اتوماتیک پایۀ گاز FM200

## Summary
[6 empty] | Date: | 1396/10/22
[6 empty] | Revision | 38.3
Ali Cheraghi
FM-200 Fire Suppression System
Total Flooding method
Project Information
Project Name : | Insert Project Name |  |  |  | DATE : | 1389/10/10
Contractor : | Client
Tel : |  |  |  |  | Contact : | Mr.
Fax :
Address :
Calculated by: |  |  |  |  | Title :
Attention:
This Software designed for FM-200 basic PreCalculation. Final Calculation Must be done by Specialist Technicians via Specified Tyco, THORN or LPG Software Programs.
Insert Data
Agent Calculation Result
Brand Selected |  | THORN |  | Low Pressure FM-200 System
Total quantity of FM 200 required |  | 98 | Kg
Size of Container requierd |  | 147 | liter | Number of Container requierd |  |  | 1
Estimating Number of Nozzles |  | 4

## raw data (hidden)
Design Standards | Fire Classification |  | 1
NFPA 2001 | A |  | NFPA | According to NFPA 2001 (2015 Edition)(Table A.5.4.2.2 (b)) Minimum 7 % Design Concentration is Recommend for Class C of Fires | 1 | 7 | 1
ISO 14520 - 9 | B |  | ISO | According to ISO14520 Minimum 8.5 % Design Concentration is Recommend for Higher Hazard Class A of Fires | 0 | 8.5 | 2
FM | C |  | FM | According to FM Minimum 7.17 % Design Concentration is Recommend for Class C of Fires | 0 | 7.17 | 3
Vds 2381 |  |  | Vds | According to Vds Minimum 7.2 % Design Concentration is Recommend for Class C of Fires | 0 | 7.2 | 4
EN 15004 - 5 |  |  | EN | According to EN 15004 Minimum 8.5 % Design Concentration is Recommend for Higher Hazard Class A of Fires | 0 | 8.5 | 5
According to NFPA 2001 (2015 Edition)(Table A.5.4.2.2 (b)) Minimum 7 % Design Concentration is Recommend for Class C of Fires
Supplier | THORN_Cylinders_Volume | THORN | LPG | Cylinder Size
THORN | 4.5 | 4.5 | 5 | 4.5 |  |  |  | 74.0 to 147.0 | THORN Filling
LPG | 8 | 8 | 13.4 | 8 |  |  |  | 0 | LPG Filling
| 16 | 16 | 26.8 | 16 |  |  |  | 303.205.020 | THORN Part Number
| 32 | 32 | 40.2 | 32 |  |  |  | 0 | LPG Part Number | Master c/w solenoid
| 52 | 52 | 67 | 52 |  |  |  | FALSE | LPG Part Number | Master c/w 1/8" solenoid
| 106 | 106 | 75 | 106 |  |  |  | FALSE | LPG Part Number | Master c/w 1/8" solenoid
| 147 | 147 | 100 | 147 |  |  |  | FALSE | LPG Part Number | Slave c/w blind cap
| 180 | 180 | 120 | 180
| 5 | [6 empty] | 74 | Min. THORN Filling
| 13.4 | [6 empty] | 0 | Min. LPG Filling
| 26.8 | [6 empty] | 147 | Max. THORN Filling
| 40.2 | [6 empty] | 0 | Max. LPG Filling
67
75
| 100 |  | Nozzle location is affected by the shape of the hazard area. 1- The maximum discharge radius is 8.7 m for a 360° nozzle and 10.05 m for a 180° nozzle. 2- The maximum coverage area for either nozzle is 95.3 m². 3- 4.87 m maximum protection height for 360° and 180° nozzle. 4- 300 mm minimum void height. (i.e. Sub-floors and false ceilings) 5- 180° nozzles must be mounted adjacent to a wall and must be located to cover the entire area. 6- Maximum distance 180 degree nozzles should be placed from a wall 300 mm, the minimum 50 mm. Measured from centre of the nozzle to the wall. 7- To avoid turbulences inside the hazard the quantity per nozzle should not exceed 100 kg.
120
Nozzle location is affected by the shape of the hazard area. 1- The maximum discharge radius is 4.2 m for a 360° nozzle and 6.7 m for a 180° nozzle. 2- Maxium protection area per nozzle is 36 m2. 3- 4.1 m maximum protection height for 360° and 180° nozzle. 4- 460mm minimum hight. 5- 360° nozzles to be placed as close to the center of the hazard as possible. 6- 180° nozzles to be preferable placed on the longer side wall, max. 300 mm away from the wall. 7- On multiple nozzle systems, the nozzles should be as equally spaced as possible. 8- To avoid turbulences inside the hazard the quantity per nozzle should not exceed 100 kg.

## Protected Areas
[15 empty] | Date: | 1396/10/22 | 1396/10/22
[15 empty] | Revision | 38.3 | 38.3
Ali Cheraghi
FM-200 Fire Suppression System | [17 empty] | back to Summary
Total Flooding method | [17 empty] | go to Flow Rate
Insert Project Name
Design Standard |  |  | NFPA 2001
1
Discharge Time |  |  | 6 - 10 second |  |  |  | NFPA 2001 (2015 Edition), 5.7.1.1.1: For halocarbon agents, the discharge time required to achieve 95% of the M.D.C. for flame extinguishment based on a 20 percent safety factor shall not exceed 10 seconds
Fire Classification |  |  | C |  |  |  | NFPA 1, 3.3.102.3: Class C fires are fires that involve energized electrical equipment.
3
Minimum Design Concentration |  |  | 7 |  | % |  | Selectable Standard M.D.C. |  |  |  | Select Fule M.D.C
According to NFPA 2001 (2015 Edition)(Table A.5.4.2.2 (b)) Minimum 7 % Design Concentration is Recommend for Class C of Fires
Insert Desirable M.D.C. Manually |  |  | 7 |  | %
Min. Design Concentration Set: |  |  | 7 |  | % |  | Your Inserted M.D.C Used for Calculation
Min. Anticipated Temperature |  |  | 18 |  | °c | [5 empty] | Specific Vapour Volume (Min. Temp) |  |  | 0.13614 |  | m3/kg
Max. Anticipated Temperature |  |  | 28 |  | °c | [5 empty] | Specific Vapour Volume (Max. Temp) |  |  | 0.14127 |  | m3/kg | m3/kg
[11 empty] | Specific Vapour Volume (NFPA) |  |  | 0.1373 |  | m3/kg | m3/kg
Number of Hazard (Enclosures) |  |  | 3 | [7 empty] | Total Volume |  | 190 | m3
Info. Only
Hazard No. | Hazard Name |  |  | Length | Width | Height | Boundary Area | Hazard Area | Hazard Volume | Non-permeable Volume | Total Volume | Percent of Volume/Total | Basic Aget Quantity | Calculated Total Aget Qty |  | Aget Quantity |  | Max. Concentration/Hazard
|  |  |  | m | m | m | m2 | m2 | m3 | m3 | m3 | % | kg | kg |  | kg |  | %
1 | Server Room |  |  | 10 | 5 | 3 | 190 | 50 | 150 | 0 | 150 | 78.95% | 82.9343 | 77.3684 |  | 77.2164 | 0 | 7.5264
2 | Server Room, Suspend Ceiling |  |  | 10 | 5 | 0.4 | 112 | 50 | 20 | 0 | 20 | 10.53% | 11.0579 | 10.3158 |  | 10.2955 | 0 | 7.5264
3 | Server Room, Rised Floor |  |  | 10 | 5 | 0.4 | 112 | 50 | 20 | 0 | 20 | 10.53% | 11.0579 | 10.3158 |  | 10.2955 | 0 | 7.5674
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 |  | 0 | 0 | #DIV/0!
[7 empty] | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 |  | 0 | 0 | #DIV/0!
97.8074
[10 empty] | Q1= | Total Basic Agent |  | 105.0501 | kg
SEA LEVEL |  |  | 1200 |  | m | #NAME? | [5 empty] | Correction Factors |  | 0.89 |  | kg | kg
NFPA 2001 (2015 Edition),5.5.3.3: Design Factor for Enclosure Pressure. The design quantity of the clean agent shall be adjusted to compensate for ambient pressures that vary more than 11 percent [equivalent to approximately 915 m of elevation change] from standard sea level pressures [29.92 in. Hg at 70°F (760 mm Hgat 0°C)].
[11 empty] | Q2= | Calculated Agent weight |  | 93.4946 |  | kg | kg
Set Agent weight to |  |  | 98 |  | kg | [5 empty] | Q3= | Total Agent required |  | 98 |  | Kg | Kg
0
[10 empty] | Predict Achieved |  | Concentration Minimum |  | 7.3127 |  | % | %
[12 empty] | Concentration Maximum |  | 7.5674 |  | % | %
0
Select Favorite Brand |  |  | THORN | [8 empty] | THORN | LPG
Cylinder Size |  |  | 147 |  | Liter | [6 empty] | Cylinder Min. & Max. of Filling |  |  | 74.0 to 147.0 | kg | kg
Number of Cylinders |  |  | 1 | [8 empty] | Cylinder Part Number |  | 1 | 303.205.020
[12 empty] | Cylinder Part Number |  | 0
[12 empty] | Filling Per Cylinder |  |  | 98
0
NFPA 2001 (2015 Edition), 4.1.3.2: Storage containers shall be located as close as possible to or within the hazard or hazards they protect.
NFPA 2001 (2015 Edition), 4.1.3.3 Agent storage containers shall not be located where they can be rendered inoperable or unreliable due to mechanical damage or exposure to chemicals or harsh weather conditions or by any other foreseeable cause. Where container exposure to such conditions is unavoidable, then suitable enclosures or protective measures shall be employed.
NFPA 2001 (2015 Edition), 4.1.4.5: The containers connected to a manifold shall meet the following criteria: (1) For halocarbon clean agents in a multiple container system, all containers supplying the same manifold outlet for distribution of the same agent shall be interchangeable and of one select size and charge.
NFPA 2001 (2015 Edition), 5.3.4: To prevent loss of agent through openings to adjacent hazards or work areas, openings shall be permanently sealed or equipped with automatic closures. Where reasonable confinement of agent is not practicable, protection shall be expanded to include the adjacent connected hazards or work areas or additional agent shall be introduced into the protected enclosure using an extended discharge configuration.
NFPA 2001 (2015 Edition), 5.6: Duration of Protection. A minimum concentration of 85 percent of the design concentration shall be held at the highest level of combustibles for a minimum period of 10 minutes or for a time period to allow for response by trained personnel. It is important that the agent design concentration not only shall be achieved, but also shall be maintained for the specified period of time to allow effective emergency action by trained personnel. This is equally important in all classes of fires, since a persistentignition source (e.g., an arc, heat source, oxyacetylene torch, or “deep-seated” fire) can lead to resurgence of the initial event once the clean agent has dissipated.
Note on M15: Ali: Select Appropriate M.D.C. According to table
Note on A19: Ali: Manually Selected M.D.C. shall be equal or greater then Standard Recommandation
Note on P26: Ali: Higher agent concentration if the system discharges at Tmax
Note on M28: Ali: According to NFPA 2001 (2015 Edition), Table A.5.5.1 (j)
Note on E30: You can select 5 parts (hazard) for each sector that extinguish simultaneous (calculation will be perfored based on involved enclosure who that you selected): Expamle: 1-Main Area 2-Main Area & Suspend Ceiling 3-Main Area & Suspend Ceiling & Rised Floor 4- Other Part 5- Other Part for each part, you have to insert its data to corrected sheet.
Note on L33: Ali: Volume of Fixed parts (such as fixed structure or fixed Non-permeable equipment) inside protected area can be deduce from total hazard volume
Note on O33: Ali: NFPA 2001 (2015 Edition), 5.5 Total Flooding Quantity
Note on P33: Ali: Total Agent Required for each hazard
Note on R33: Ali: NFPA 2001 (2015 Edition), Table A.5.5.1 (j) ONLY for INFORMATIOM
Note on U33: Ali: NFPA 2001 (2015 Edition), 5.5 Total Flooding Quantity
Note on A46: Ali: NFPA2001 (2015 Edition), Table 5.5.3.3 Design Factor for Enclosure Pressure. The design quantity of the clean agent shall be adjusted to compensate for ambient pressures that vary more than 11 percent [equivalent to approximately 3000 ft (915 m) of elevation change] from standard sea level pressures
Note on A53: Ali Cheraghi: Agent weight must be rounded UP to a correct value
Note on A65: Ali Cheraghi: THORN product is Low Pressure System LPG product is High Pressure System
Note on A66: Ali Cheraghi: CylinderVolume must be selected Manually According to Agent Volume & Supplier Please Pay Attention to Minimum & Maximum Filling of each container
Note on A67: Ali Cheraghi: Select Number of Cylinder Required for the Volume of Gas Specified

## Nozzle & Flow Rate
[20 empty] | Date: | 1396/10/22
[20 empty] | Revision | 38.3
Ali Cheraghi
FM-200 Fire Suppression System
Nozzle & Flow Rate | [21 empty] | back to PROTECTED AREAS
Insert Project Name
Discharge Time is between 6 to 10 Seconds
Selected Brand |  |  | THORN | Low Pressure System
General Rules for Selecting Number of Nozzles:
Nozzle location is affected by the shape of the hazard area. 1- The maximum discharge radius is 8.7 m for a 360° nozzle and 10.05 m for a 180° nozzle. 2- The maximum coverage area for either nozzle is 95.3 m². 3- 4.87 m maximum protection height for 360° and 180° nozzle. 4- 300 mm minimum void height. (i.e. Sub-floors and false ceilings) 5- 180° nozzles must be mounted adjacent to a wall and must be located to cover the entire area. 6- Maximum distance 180 degree nozzles should be placed from a wall 300 mm, the minimum 50 mm. Measured from centre of the nozzle to the wall. 7- To avoid turbulences inside the hazard the quantity per nozzle should not exceed 100 kg.
Number of Enclosures |  |  | 3 | [14 empty] | Total Volume |  | 190 | m3
[18 empty] | Total Agent |  | 98 | kg
Sector No. | Hazard Name |  |  | Length | Width | Height | Boundary Area | Hazard Area | Hazard Volume | Total Volume | Percent of Volume/Total | Total Aget Quantity | System Flow Rate |  | Flow rate/Hazard |  | Number of Nozzle |  | Agent/ Nozzle | Flow Rate/Nozzle
[13 empty] | Max. | Min. | Max. | Min. | recommend | set to |  | Max. | Min.
|  |  |  | m | m | m | m2 | m3 | m3 | m3 | % | kg | kg/second |  | kg/second |  | pcs | pcs | kg | kg/second
1 | Server Room |  |  | 10 | 5 | 3 | 50 | 150 | 0 | 150 | 78.95% | 77.3684 | 17.5083 | 10.505 | 12.8947 | 7.7368 | 1 | 2 | 38.6842 | 6.4474 | 3.8684 | 1 | 1 | 1 | 2 | 2 | 2
2 | Server Room, Suspend Ceiling |  |  | 10 | 5 | 0.4 | 50 | 20 | 0 | 20 | 10.53% | 10.3158 |  |  | 1.7193 | 1.0316 | 1 | 1 | 10.3158 | 1.7193 | 1.0316 | 1 | 1 | 1 | 2 | 2 | 2
3 | Server Room, Rised Floor |  |  | 10 | 5 | 0.4 | 50 | 20 | 0 | 20 | 10.53% | 10.3158 |  |  | 1.7193 | 1.0316 | 1 | 1 | 10.3158 | 1.7193 | 1.0316 | 1 | 1 | 1 | 2 | 2 | 2
0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 |  |  | 0 | 0 | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0!
0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 |  |  | 0 | 0 | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0! | 0 | #DIV/0! | #DIV/0!
[17 empty] | Your Estimating Nozzle |  |  | 4
50
0
0

## THORN Cylinder
THORN Security
Containers Detail
UL/FM Approved
back to CALCULATION sheet (Protected Areas)
Set Agent weight to |  | 98 |  | kg |  |  |  |  | Cylinder Selected |  | 147 |  | Liter
[9 empty] | Number of Cylinder |  | 1
Nominal Volume | Part Number | Minimum & Maximum Filling |  |  |  | Outlet Size |  | Dimension A |  | Diameter |  | Empty Weight
|  | Kg |  |  | (Lbs.) | mm | In | mm | In | mm | In | Kg | Ibs
4.5 liter | 303.205.025 | 2.3 | to | 4.5 | 5 to 10 | 25 | 1" | 280 | 11" | 178 | 7" | 7.7 | 17
8 liter | 303.205.015 | 4 | to | 8 | 10 to 18 | 25 | 1" | 304 | 12" | 254 | 10" | 14.8 | 32.6
16 liter | 303.205.016 | 8 | to | 16 | 20 to 39 | 25 | 1" | 502 | 19.8" | 254 | 10" | 18.4 | 40.6
32 liter | 303.205.017 | 16 | to | 32 | 38 to 74 | 25 | 1" | 833 | 32.8" | 254 | 10" | 26.1 | 57.5
40 liter * | 303.205.030 | 20 | to | 40 | 48 to 95 | 50 | 2" | 1352 | 53.2" | 227.2 | 9" | 52.2 | 115
52 liter | 303.205.018 | 26 | to | 52 | 59 to 117 | 50 | 2" | 596 | 23.5" | 406 | 16" | 49.1 | 108.3
67.5 liter * | 303.205.031 | 33.8 | to | 67.5 | 74 to 147 | 50 | 2" | 1526 | 60" | 265 | 10.4" | 81.6 | 180
80 liter * | 303.205.032 | 40 | to | 80 | 91 to 180 | 50 | 2" | 1685 | 66.3" | 276 | 11" | 95.3 | 210
106liter | 303.205.019 | 53 | to | 106 | 118 to 235 | 50 | 2" | 1021 | 40.2" | 406 | 16" | 71.8 | 158.3
147liter | 303.205.020 | 74 | to | 147 | 163 to 325 | 50 | 2" | 1354 | 53.3" | 406 | 16" | 89.9 | 198.2
180liter | 303.205.021 | 90 | to | 180 | 201 to 401 | 50 | 2" | 1634 | 64.3" | 406 | 16" | 105.8 | 233.2
343liter* | 303.205.022 | 172 | to | 343 | 379 to757 | 89 | 3.5" | 1466 | 57.7 | 610 | 24" | 207 | 456
* UL Listed Systems Only (Not FM Approved) - NOT Supply

## LPG Cylinder
LPG
Containers Detail
UL & LPCB Approved
Set Agent weight to |  | 0 | Kg | Only High Pressure Cylinders Supplied | [5 empty] | Cylinder Selected |  | 0 | Liter | back to CALCULATION sheet (Protected Areas)
[10 empty] | Number of Cylinder |  | 0
Please going to THORN Cylinder Tab for Cylinder Selection
Part Number | Cylinder Type | Cylinder | Pressure | Construction | Valve | Pressure Gauge Rated | Safety Disk | Outlet | Diameter | Cylinder Length | Valve Length | Minimum & Maximum Filling
|  | Liter | bar | [5 empty] | mm | mm | mm | kg
|  | 240 | 25 bar | Welded | LPG-230 |  |  | 2½" (65mm) | 455 | 1625±10 | 308 (LP-230) | 115.2 | 276
|  | 175 | (60bar T.P) | [5 empty] | 455 | 1220±10 |  | 84 | 201.2
|  | 142 | [6 empty] | 401.2 | 1273±10 |  | 68.2 | 163.3
75025002 | Master c/w solenoid | 120 | 25 bar 42 bar (250bar T.P) | Seamless | LPG 190-55 (LP 25 bar) | 0-69 bar | 60±3bar | 1½" (40mm) | 357 | 1470±20 | 180 (LPG190) | 57.6 | 138
75025005 | Master c/w 1/8" solenoid
75025007 | Slave c/w blind cap
74102003 | Master c/w solenoid | 100 | [6 empty] | 357 | 1314±20 |  | 48 | 115
74102010 | Master c/w 1/8" solenoid
74025422 | Slave c/w blind cap |  |  |  | LPG 190-50 (HP 42 bar) | 0-103 bar | 95±7bar
72025421 | Master c/w solenoid | 75 | [6 empty] | 267 | 1273±10 |  | 36 | 86.2
72025423 | Master c/w 1/8" solenoid
72025425 | Slave c/w blind cap
71025420 | Master c/w solenoid | 67 | 25 bar 42 bar (250bar T.P) | Seamless | LPG 145-55 (LP 25 bar) | 0-69 bar | 60±3bar | 1" (25mm) | 267 |  | 165 (LPG145) | 32.4 | 77
71025423 | Master c/w 1/8" solenoid
71025425 | Slave c/w blind cap
70025452 | Master c/w solenoid | 40.2 |  |  | LPG 145-50 (HP 42 bar) | 0-103 bar | 95±7bar |  | 229 |  |  | 19.3 | 46.2
70025462 | Slave c/w blind cap
70025448 | Master c/w solenoid | 26.8 | 25 bar 42 bar (250bar T.P) | Seamless | LPG 128-55 (LP 25 bar) | 0-69 bar | 60±3bar | ¾" (20mm) | 229 |  | 148 (LPG128) | 12.9 | 30.8
70025460 | Slave c/w blind cap
70025444 | Master c/w solenoid | 13.4 | [6 empty] | 140 |  |  | 6.5 | 15.4
70025458 | Slave c/w blind cap |  |  |  | LPG 128-50 (HP 42 bar) | 0-103 bar | 95±7bar
70025441 | Master c/w solenoid | 5 | [6 empty] | 140 |  |  | 2.4 | 5.7
70025456 | Slave c/w blind cap
* OInly High Pressure Cylinder Supplied

## Pipe (hidden)
FM 200 Fire Suppression System
Estimating of Pipe Size
Insert Project Name
Max. Flow Rate |  |  | #NAME? | Kg/Sec |  | Min. Flow Rate |  | #NAME? | Kg/Sec | back to CALCULATION sheet
back to NOZZLE & FLOW sheet
Max. Flow Rate per Nozzle Area 1 |  |  | #NAME? | Kg/Sec |  | Min. Flow Rate per Nozzle |  | #NAME? | Kg/Sec
Max. Flow Rate per Nozzle Area 2 |  |  | #NAME? | Kg/Sec |  | Min. Flow Rate per Nozzle |  | #NAME? | Kg/Sec
Max. Flow Rate per Nozzle Area 3 |  |  | #NAME? | Kg/Sec |  | Min. Flow Rate per Nozzle |  | #NAME? | Kg/Sec
| Max. & Min. Flow Rates. |  | Pipe Size |  | Minimum flow rate |  | Maximum flow rate
|  |  | mm | inch | kg/sec. |  | kg/sec.
|  |  | 10 | 3/8 | 0.272 |  | 0.907
|  |  | 15 | 1/2 | 0.454 |  | 1.361
|  |  | 20 | 3/4 | 0.907 |  | 2.495
|  |  | 25 | 1 | 1.588 |  | 3.855
|  |  | 32 | 1 1/4 | 2.722 |  | 5.67
|  |  | 40 | 1 1/2 | 4.082 |  | 9.072
|  |  | 50 | 2 | 6.35 |  | 13.61
|  |  | 65 | 2 1/2 | 9.072 |  | 24.95
|  |  | 80 | 3 | 13.61 |  | 44.92
|  |  | 100 | 4 | 24.95 |  | 56.7
|  |  | 125 | 5 | 40.82 |  | 90.72
|  |  | 150 | 6 | 54.43 |  | 136.1
|  | Pipe and nozzle sizes need to be confirmed by the computer program. | Note: This information is for Schedule 40 pipe, and serves as an estimate only.

## Altitude
[6 empty] | Date: | 1396/10/22
[6 empty] | Revision | 38.3
Ali Cheraghi
FM-200 Fire Suppression System | [7 empty] | back to Protected Areas
Total Flooding method
Insert Project Name
Sea Level |  |  | 1200 | m
Correction Factor |  |  | 0.89
Altitude Correction Factors
NFPA2001 (2015 Edition), Table 5.5.3.3
Equivalent Altitude |  |  | Enclosure Pressure (Absolute) |  | Correction Factor
Foots | Km | Meters | psi | mm Hg
-3000 | -0.92 | -920 | 16.25 | 840 | 1.11 |  |  | 0.89
-2000 | -0.61 | -610 | 15.71 | 812 | 1.07 |  |  | 0.89
-1000 | -0.3 | -300 | 15.22 | 787 | 1.04 |  |  | 0.89
0 | 0 | 0 | 14.7 | 760 | 1 |  |  | 0.89
1000 | 0.3 | 300 | 14.18 | 733 | 0.96 |  |  | 0.89
2000 | 0.61 | 610 | 13.64 | 705 | 0.93 |  |  | 0.89
3000 | 0.91 | 910 | 13.12 | 678 | 0.89 |  |  | 0.89
4000 | 1.22 | 1220 | 12.57 | 650 | 0.86 |  |  | 0.89
5000 | 1.52 | 1520 | 12.03 | 622 | 0.82 |  |  | 0
6000 | 1.83 | 1830 | 11.53 | 596 | 0.78 |  |  | 0
7000 | 2.13 | 2130 | 11.03 | 570 | 0.75 |  |  | 0
8000 | 2.45 | 2450 | 10.64 | 550 | 0.72 |  |  | 0
9000 | 2.74 | 2740 | 10.21 | 528 | 0.69 |  |  | 0
10000 | 3.05 | 3050 | 9.77 | 505 | 0.66 |  |  | 0

## NFPA S.V.V
[12 empty] | Date: | 1396/10/22
[12 empty] | Revision | 38.3
Ali Cheraghi
FM-200 Fire Suppression System | [15 empty] | back to Summary
Total Flooding method | [15 empty] | back to Protected Areas
Insert Project Name
| Minimum Temperature |  | 18 |  | °c |  |  |  | Specific Vapour Volume |  |  | 0.1373
| Min. Design Concentration |  | 7 |  | % |  |  |  | Agent Weight Requirements |  |  | 0.5784 | kg/m3
FM 200 Total Flooding Quantity (NFPA2001 (2015 Edition)-Table A.5.5.1(j))
Design Temperature of Hazard Area (t) |  | Specific Vapour Volume of FM200 at Design Temp. (s) m3/Kg |  | Concentration ( C ) %
|  |  |  | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
Agent Weight Requirements (kg/cu.m)
-10 |  | 0.1215 |  | 0.5254 | 0.6515 | 0.7158 | 0.8142 | 0.9147 | 1.0174 | 1.1225 | 1.2301 | 1.3401 | 1.4527 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
-5 |  | 0.1241 |  | 0.5142 | 0.638 | 0.7005 | 0.7987 | 0.8951 | 0.9957 | 1.0985 | 1.2038 | 1.3114 | 1.4216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 |  | 0.1268 |  | 0.5034 | 0.6251 | 0.6858 | 0.78 | 0.8763 | 0.9748 | 1.0755 | 1.1785 | 1.2839 | 1.3918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 |  | 0.1294 |  | 0.4932 | 0.6128 | 0.6719 | 0.7642 | 0.8586 | 0.955 | 1.0537 | 1.1546 | 1.2579 | 1.3636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 |  | 0.132 |  | 0.4834 | 0.6008 | 0.6585 | 0.749 | 0.8414 | 0.936 | 1.0327 | 1.1316 | 1.2328 | 1.2264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 |  | 0.1347 |  | 0.474 | 0.5894 | 0.6457 | 0.7344 | 0.8251 | 0.9178 | 1.0126 | 1.1096 | 1.2089 | 1.3105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 |  | 0.1373 |  | 0.465 | 0.5784 | 0.6335 | 0.7205 | 0.8094 | 0.9004 | 0.9934 | 1.0886 | 1.1859 | 1.2856 | 1 | 0.5784 | 0.5784 | 0.6335 | 0.7205 | 0.8094 | 0.9004 | 0.9934 | 1.0886 | 1.1859 | 1.2856 | 0.5784
25 |  | 0.1399 |  | 0.4564 | 0.5678 | 0.6217 | 0.7071 | 0.7944 | 0.8837 | 0.975 | 1.0684 | 1.164 | 1.2618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 |  | 0.1425 |  | 0.4481 | 0.5575 | 0.6104 | 0.6943 | 0.78 | 0.8676 | 0.9573 | 1.049 | 1.1428 | 1.2388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 |  | 0.145 |  | 0.4401 | 0.5476 | 0.5996 | 0.6819 | 0.7661 | 0.8522 | 0.9402 | 1.0303 | 1.1224 | 1.2168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
40 |  | 0.1476 |  | 0.4324 | 0.5381 | 0.5891 | 0.6701 | 0.7528 | 0.8374 | 0.923 | 1.0124 | 1.1029 | 1.1956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
45 |  | 0.1502 |  | 0.425 | 0.5289 | 0.579 | 0.6586 | 0.7399 | 0.823 | 0.908 | 0.995 | 1.084 | 1.1751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
50 |  | 0.1527 |  | 0.418 | 0.52 | 0.5694 | 0.6476 | 0.7276 | 0.8093 | 0.8929 | 0.9784 | 1.066 | 1.1555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 |  | 0.1553 |  | 0.4111 | 0.5114 | 0.56 | 0.6369 | 0.7156 | 0.796 | 0.8782 | 0.9623 | 1.0484 | 1.1365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 |  | 0.1578 |  | 0.4045 | 0.5031 | 0.551 | 0.6267 | 0.7041 | 0.7832 | 0.8641 | 0.9469 | 1.0316 | 1.1183 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 |  | 0.1604 |  | 0.398 | 0.495 | 0.5423 | 0.6167 | 0.6929 | 0.7707 | 0.8504 | 0.9318 | 1.0152 | 1.1005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
70 |  | 0.1629 |  | 0.3919 | 0.4872 | 0.5338 | 0.6072 | 0.6821 | 0.7588 | 0.8371 | 0.9173 | 0.9994 | 1.0834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
75 |  | 0.1654 |  | 0.3859 | 0.4797 | 0.5257 | 0.5979 | 0.6717 | 0.7471 | 0.8243 | 0.9033 | 0.9841 | 1.0668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
80 |  | 0.1679 |  | 0.3801 | 0.4724 | 0.5178 | 0.0589 | 0.6617 | 0.736 | 0.812 | 0.8898 | 0.9694 | 1.0509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
85 |  | 0.1704 |  | 0.3745 | 0.4652 | 0.5102 | 0.5803 | 0.6519 | 0.7251 | 0.8 | 0.8767 | 0.9551 | 1.0354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
90 |  | 0.173 |  | 0.369 | 0.4584 | 0.5027 | 0.5717 | 0.6423 | 0.7145 | 0.7883 | 0.8638 | 0.9411 | 1.0202 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0.1373
0.1425
0.1629

## Fule M.D.C
Minimum FM 200 Design Concentration |  | back to Protected Area sheet
FUEL | Minimum Design Concentration ( % )
Acetylene | 66
Acetone | 9.1
Acetonitrile | 8
t-Amyl Alcohol | 9.6
AV Gas | 8.6
Benzene | 8
n-Butane | 8.7
n-Butanol | 10
2-Butoxyethanol | 9.8
2-Butoxyethyl Acetate | 9.1
n-Butyl Acetate | 9.2
Carbon disulphide | 15.6
Chloroethane | 8.3
Crude Oil | 8.6
Cyclohexane | 9.5
Cyclohexylamine | 8.8
Cyclopentanone | 9.8
1,2-Dichloroethane | 8
Diesel | 8.8
N,N-Diethylanolamine | 10.3
Diethyl Ether | 9.9
Ethane | 8.8
Ethanol | 11
Ethyl Acetate | 9
Ethyl Benzene | 8.3
Ethylene | 11.1
Ethylene Glycol | 10
Gasoline | 9.1
Heptane | 8
n-Hexane | 9.1
l-Hexene | 8
Hydraulic Fluid | 8.6
Hydraulic Oil | 8
Hydrogen | 17.4
Isobutyl Alcohol | 10
Isopropanol | 9.9
JP4 | 9.1
JP5 | 9.1
Kerosene | 9.8
Methane | 8
Methanol | 13.7
2,Methoxyethanol | 12.4
Methyl Ethyl Ketone | 9.8
Methyl Isobutyl Ketone | 9.2
Mineral Spirits | 8.7
Morpholine | 10.4
Nitromethane | 13.1
n-Pentane | 9
Propane | 8.8
l-Propanol | 10.2
Propylene | 8.2
Propylene Glycol | 11.4
Pyrrollidine | 9.6
Tetrahydrofuran | 9.8
Tetrahydrothiophene | 8.7
Toluene | 8
Tolylene-2,4-diisocyanat | 8
Transformer Oil | 9.6
Xylene | 8

## M.D.C ( MARIN ) (hidden)
NOOR NEDA System Co.
Minimum FM 200 Design Concentration |  | Back
FUEL | Minimum Design Concentration ( % )
Acetylene | 66
Acetone | 9
Acetonitrile | 8.7
t-Amyl Alcohol | 9.5
AV Gas | 8.7
Benzene | 8.7
n-Butane | 8.7
n-Butanol | 9.9
2-Butoxyethanol | 9.6
2-Butoxyethyl Acetate | 9
n-Butyl Acetate | 9.1
Carbon disulphide | 15.3
Chloroethane | 8.7
Crude Oil | 8.7
Cyclohexane | 9.4
Cyclohexylamine | 8.7
Cyclopentanone | 9.6
1,2-Dichloroethane | 8.7
Diesel | 8.7
N,N-Diethylanolamine | 10.1
Diethyl Ether | 9.8
Ethane | 8.7
Ethanol | 10.8
Ethyl Acetate | 8.8
Ethyl Benzene | 8.7
Ethylene | 10.9
Ethylene Glycol | 9.9
Gasoline | 9
n-Heptane | 8.7
n-Hexane | 9
l-Hexene | 8.7
Hydraulic Fluid | 8.7
Hydraulic Oil | 8.7
Hydrogen | 17.2
Isobutyl Alcohol | 9.9
Isopropanol | 9.8
JP4 | 9
JP5 | 9
Kerosene | 9.6
Methane | 8.7
Methanol | 13.5
2,Methoxyethanol | 12.2
Methyl Ethyl Ketone | 9.6
Methyl Isobutyl Ketone | 9.1
Mineral Spirits | 8.7
Morpholine | 10.3
Nitromethane | 12.9
n-Pentane | 8.8
Propane | 8.7
l-Propanol | 10
Propylene | 8.7
Propylene Glycol | 11.2
Pyrrolidine | 9.5
Tetrahydrofuran | 9.6
Tetrahydrothiophene | 8.7
Toluene | 8.7
Tolylene-2,4-diisocyanat | 8.7
Transformer Oil | 9.5
Xylene | 8.7

## FM 200 Info. (hidden)
FM-200 extinguishes by causing a chemical reaction with the combustion products, and does not remove oxygen like CO2 and other inert agents. Therefore, exposure to FM-200 at the design concentration of 7.17%, and up to 9.0%, is not hazardous to health. FM-200 can decompose at high temperatures to form halogen acids.
FM-200 (HFC-227ea) is a clean, gaseous agent containing no particles or oily residues.
FM-200 is thermally and chemically stable, but with-out the extremely long atmospheric lifetimes associated with other proposed halon replacements. The atmospheric lifetime of FM-200 has been determined to be 36.5 years (Reference GLCC).
Agent Physical Properties
Agent Physical Properties | HFC-227ea |  | Agent Physical Properties | HFC-227ea
Chemical structure | CF3CHFCF3 |  | Chemical structure | N2
Chemical name | Heptafluoropropan |  | Chemical name | Nitrogen
Molecular weight | 170.03 |  | Molecular weight | 28.0
Boiling point | -16.4 0ºC (1.9ºF) |  | Boiling point | -195.8ºC (-320.4ºF)
Freezing point | -131.1ºC (-204ºF) |  | Freezing point | -210.0ºC (-346ºF)
Critical temperature | 101.7ºC (214ºF) |  | Critical temperature | -146.9ºC (-232.4ºF)
Critical pressure | 2912 kPa (422 psi) |  | Critical pressure | 3399 kPa (492.9 psi)
Critical volume | 274 cc/mole (.0258cu Ft./lb.) |  | Saturated vapour density @20o C (68 o F) | 31.18 k /m 3 (1.95 lb./ft 3)
Critical density | 621 kg /m3 (38.76 lb./Ft 3) |  | (Reference:NFPA 2001,2000 edition)
Saturated vapour density @20oC (68 o F) | 31.18 k /m 3 (1.95 lb./ft 3)
(Reference:NFPA 2001,2000 edition)
Toxicology/Environmental
Environmental |  |  | Agent Physical Properties | HFC-227ea
Ozone Depletion (ODP) |  | 0 | Physical State | Liquefied Compressed Gas
Atmospheric Lifetime (yrs) (Reference:Great Lakes Chemical Corporation) |  | 36.5 | Colour | Colourless
Toxicology |  |  | Odour | Odourless
Acute Exposure LC (ppm) |  | >800,000 | Vapour Pressure | 58.8 psia at 21°C
Cardiac Sensitization |  |  | Specific Gravity | 1.48
No Observed Adverse Effect Level (NOAEL) |  | 9% | Solubility | Not available
Lowest Observed Adverse Effect Level (LOAEL) (Reference: NFPA 2001,2000 edition) |  | >10.5% | pH | Not Applicable
|  |  | Viscosity | Not Applicable
|  |  | Vapour Density | Not Available
|  |  | Flash Point | None
|  |  | Flammable Limits | None
|  |  | Autoignition Temperature | None

## 1.Container (hidden)
NOOR NEDA System Co.
FM-200® Container
| Part Number | Nom. Volume | Nom. Volume |  | Outlet Size | Dimension A | Diameter | Empty Weight
|  | Nominal Size | Kg | Lbs | mm | mm | mm | Kg
1 | 303.205.015 | 8 Litre | 4.5 to 8.0 | 10 to 18 | 25 | 304 | 254 | 14.8
2 | 303.205.016 | 16 Litre | 9.0 to 17.5 | 20 to 39 | 25 | 502 | 254 | 18.4
3 | 303.205.017 | 32 Litre | 17.0 to 33.5 | 38 to 74 | 25 | 833 | 254 | 26.1
4 | 303.205.030 | 40 Litre | 22.0 to 43.0 | 48 to 95 | 50 | 1352 | 227.2 | 52.2
5 | 303.205.018 | 52 Litre | 27.0 to 53.0 | 59 to 117 | 50 | 596 | 406 | 49.1
6 | 303.205.031 | 67 Litre | 33.5 to 66.5 | 74 to 147 | 50 | 1526 | 265 | 81.6
7 | 303.205.032 | 80 Litre | 14.0 to 81.5 | 91 to 180 | 50 | 1685 | 276 | 95.3
8 | 303.205.019 | 106 Litre | 53.5 to 106.5 | 118 to 235 | 50 | 1021 | 406 | 71.8
9 | 303.205.020 | 147 Litre | 74.0 to 147.5 | 163 to 325 | 50 | 1354 | 406 | 89.9
10 | 303.205.021 | 180 Litre | 91.5 to 182.0 | 201 to 401 | 50 | 1634 | 406 | 105.8
11 | 303.205.022 | 343 Litre | 172 to 343 | 379 to 757 | 89 | 1466 | 610 | 207

## 3.NOZZELS (hidden)
NOOR NEDA System Co.
Discharge Nozzle
Nozzles are available with seven or eight ports to allow for 180° or 360° horizontal discharge patterns. Ports are drilled in 0.1mm (0.004 in) increments to the specified System design.
| Material: | Brass/Stainless Steel
| Part Number | Material:
| 310.205.028.TU | 10mm (3/8") BSP Nozzle
| 310.205.029.TU | 15mm (1/2") BSP Nozzle
| 310.205.030.TU | 20mm (3/4") BPS Nozzle
| 310.205.031.TU | 25mm (1") BSP Nozzle
| 310.205.032.TU | 32mm (1 1/4") BSP Nozzle
| 310.205.033.TU | 40mm (1 1/2") BSP Nozzle
| 310.205.034.TU | 50mm (2") BSP Nozzle
| go to TOTAL | go to FM 200 Calculation | go to NOZZEL

## Flow (hidden)
NOOR NEDA System Co.
Surface Fire |  |  | Deep Seated Fire
System Flow rate | #REF! | Kg/min | System Flow rate | #NAME? | Kg/min
Flow rate / Nozzle | #REF! | Kg/min | Flow rate / Nozzle | #NAME? | Kg/min

## Opening Loss (hidden)
NOOR NEDA System Co.
#REF!
| Design Concentration | #REF! | %
|  | m |  | ft
| Please Enter Opening centered from below ceiling | #REF! | Convert | #REF!
|  | Lb/min·ft2 |  | kg/min·m2
| Please Enter Leakage Rate | 0 | Convert | 0
Go to Surface Fire
Go to Deep seated Fire